## Read Me
Villa Somalia SCADA – Project Bill of Material
Project | Solarization Villa Somalia – Power Plant Control & SCADA System
Client | Ministry of Energy & Water Resources – Somalia
Contractor | Blueflag Energy Co. Ltd
Platform | Schneider Electric: Modicon M580 + X80, Modicon Edge I/O NTS, Easergy P5M30, PowerLogic PM5320, PAS600, EcoStruxure Machine SCADA Expert
Basis | Drawings BFE/PR/26/01-SCADA-001 (architecture) and -002 (communication network), I/O list docs/villa-somalia-io-list.csv, Schneider offer 'Villa Somalia' v1 and its BOM workbook.
Revision | Rev A – draft for internal review, 22-OCT-2026
How to read
BOM by Location | Every line by panel / location, with source, status and remarks. Subtotals per location.
BOM by Reference | Same items summed per part number, with offer quantity and difference.
Summary | Priced subtotal and open RFQ lines per location.
Changes vs Offer | Every quantity change, replacement, removal and addition against the Schneider offer, plus options needing a decision.
IO Capacity | Hard-wired DI/DO required by the I/O list against channels installed, with the spare margin as an input.
Cell colours
Blue text | Input: quantity, unit price or count you can change.
Yellow fill | Unit price not available yet – request a quotation (RFQ).
Green text | Value linked from another sheet.
Status values
Offered | In the Schneider offer (quantity may be corrected).
Added | Needed by the drawings or panel design; part number is a catalogue reference.
Added – ref. TBC | Needed; exact part number to be selected / confirmed with the supplier.
By others | Supplied by another package vendor; listed so the interface is not missed. Price 0.
Key open points
Prices | Unit prices are copied from the offer workbook. P5M30 and PM5320 had no price there. Currency to be confirmed.
Field switches | Five field switches and SW2 need 2 single-mode fibre ports; MCSESM083F23F1 is copper only. Select the fibre variant with Schneider.
Second CPU | The offer's second BMEP582040 is a spare. It is not a hot-standby pair (see option O2).
PVSCL60E | Removed: the site uses Sungrow SG350HX supplied by the PV EPC.
Cable lengths | Fibre, Ethernet and RS485 lengths are estimates; confirm from the cable route drawings.

## BOM by Location
Villa Somalia SCADA – Bill of Material by Location (Schneider Electric architecture, drawings BFE/PR/26/01-SCADA-001/002)
Blue = input quantity / price. Yellow = price to be obtained (RFQ). Prices in offer currency (to be confirmed).
Item | Loc | Location | Device / tag | Reference | Description | Qty | Unit | Unit price | Total price | Source | Status | Remarks
| A | Control room – SCADA, servers and network (Level 2/3)
10 | A | Control room – SCADA, servers and network (Level 2/3) | HMI-01/02 | HMIP67GD0F88BE7N00 | Harmony P6 industrial PC – operator stations (configuration per offer) | 2 | pc | 6750 | 13500 | Offer | Offered | Offer gives no description; confirm screen size, CPU and OS.
20 | A | Control room – SCADA, servers and network (Level 2/3) | HMI-01/02 | HMIEMSE3PRT4KA | EcoStruxure Machine SCADA Expert 3rd-party runtime 4K tags, digital licence | 2 | pc | 4699.914 | 9399.8279 | Offer | Offered | 4K tags per station; I/O list holds 958 signals plus internal tags.
30 | A | Control room – SCADA, servers and network (Level 2/3) | ENG-01 | HMIEMSEBT4KA | EcoStruxure Machine SCADA Expert build-time 4K tags, digital licence | 1 | pc | 2749.0325 | 2749.0325 | Offer | Offered
40 | A | Control room – SCADA, servers and network (Level 2/3) | SRV-01 | TBC-SRV-01 | SCADA server / historian, rack industrial server, RAID 1, redundant PSU, 13-month storage | 1 | pc |  |  | Sheet 001 | Added – ref. TBC | Not in offer. Needed for historian and alarm/event archive.
50 | A | Control room – SCADA, servers and network (Level 2/3) | ENG-01 | TBC-ENG-01 | Engineering workstation (laptop) with EcoStruxure Control Expert licence for M580 | 1 | pc |  |  | Sheet 001 | Added – ref. TBC | Not in offer. Needed to program and maintain the M580.
60 | A | Control room – SCADA, servers and network (Level 2/3) | GPS-01 | TBC-GPS-01 | GPS master clock with antenna, NTP / PTP server | 1 | pc |  |  | Sheet 001 | Added – ref. TBC | Time source for 1 ms relay event stamping.
70 | A | Control room – SCADA, servers and network (Level 2/3) | FW-01 | TBC-FW-01 | Industrial firewall, DMZ between Level 2 and Level 3 | 1 | pc |  |  | Sheet 001 | Added – ref. TBC | Only conduit to remote access (client policy TBC).
80 | A | Control room – SCADA, servers and network (Level 2/3) | SW1 | MCSESM083F23F1 | Modicon Extended Managed Switch 8TX – SCADA LAN (SW1) | 1 | pc | 1609.695 | 1609.695 | Offer | Offered | Offer has 2; the second is replaced by an FO variant for SW2.
90 | A | Control room – SCADA, servers and network (Level 2/3) | UPS-01 | SRT6KRMXLI | APC Smart-UPS SRT 6 kVA rack/tower, 230 V – SCADA, PLC and switches | 1 | pc |  |  | Sheet 001 | Added | Size from load list; add battery packs if > 30 min autonomy is required.
100 | A | Control room – SCADA, servers and network (Level 2/3) | UPS-01 | AP9641 | UPS Network Management Card 3 (SNMP / Modbus TCP) | 1 | pc |  |  | Sheet 002 | Added | Address 10.10.30.61.
110 | A | Control room – SCADA, servers and network (Level 2/3) | RACK-CR | AR3100 | NetShelter SX 42U 600 × 1070 mm rack – server, SW1, FW-01, GPS-01, UPS-01 | 1 | pc |  |  | Sheet 001 | Added
120 | A | Control room – SCADA, servers and network (Level 2/3) | CONSOLE | TBC-CONSOLE | Operator console, 2 positions, 2 × 27" monitors each, keyboard / mouse | 1 | lot |  |  | Sheet 001 | Added – ref. TBC | May be by building contractor.
[5 empty] | Subtotal A – Control room – SCADA, servers and network (Level 2/3) |  |  |  | 27258.5555 |  | 8 lines RFQ
| B | Main PLC panel – Drop 0 (control room)
130 | B | Main PLC panel – Drop 0 (control room) | PLC-MAIN | BMEXBP0800 | PLC 8-slot Ethernet backplane | 1 | pc | 227.682 | 227.682 | Offer | Offered
140 | B | Main PLC panel – Drop 0 (control room) | PLC-MAIN | BMXCPS3020 | X80 DC power supply 24–48 V DC, 32 W, isolated | 1 | pc | 320.0265 | 320.0265 | Offer | Offered
150 | B | Main PLC panel – Drop 0 (control room) | PLC-MAIN | BMEP582040 | M580 CPU level 2, remote and distributed I/O – plant controller (PPC) | 1 | pc | 2337.7635 | 2337.7635 | Offer | Offered | Second offer CPU is the spare (location S).
160 | B | Main PLC panel – Drop 0 (control room) | PLC-MAIN | BMENOC0311 | M580 I/O scanner module, FactoryCast, EtherNet/IP & Modbus TCP, 3 ports | 2 | pc | 887.94 | 1775.88 | Sheet 001 | Offered | #1 SCADA LAN, #2 second SCADA LAN path. Offer has 1 in use (+1).
170 | B | Main PLC panel – Drop 0 (control room) | PLC-MAIN | BMENOC0321 | M580 I/O scanner module, IP forwarding, coated – device network | 1 | pc | 1014.795 | 1014.795 | Offer | Offered
180 | B | Main PLC panel – Drop 0 (control room) | PLC-MAIN | BMXDDI3202K | X80 digital input module 32 ch 24 V DC sink | 1 | pc | 212.1705 | 212.1705 | Offer | Offered
190 | B | Main PLC panel – Drop 0 (control room) | PLC-MAIN | BMXDDO3202K | X80 digital output module 32 ch 24 V DC source | 1 | pc | 250.218 | 250.218 | Offer | Offered
200 | B | Main PLC panel – Drop 0 (control room) | PLC-MAIN | BMXFCW303 | 3 m pre-equipped cable, 1 connector + free wires (one per 32-ch module) | 2 | pc | 51.5835 | 103.167 | Offer | Offered
210 | B | Main PLC panel – Drop 0 (control room) | PLC-MAIN | ABL8RPS24100 | Phaseo power supply 24 V DC 10 A | 2 | pc |  |  | Panel design | Added | Redundant 24 V DC for PLC and I/O.
220 | B | Main PLC panel – Drop 0 (control room) | PLC-MAIN | ABL8RED24400 | Phaseo redundancy module 24 V DC 40 A | 1 | pc |  |  | Panel design | Added
230 | B | Main PLC panel – Drop 0 (control room) | PLC-MAIN | RSB1A120BD | Zelio RSB interposing relay 1 C/O 12 A, 24 V DC coil | 8 | pc |  |  | Panel design | Added | DO isolation to field circuits.
240 | B | Main PLC panel – Drop 0 (control room) | PLC-MAIN | RSZE1S35M | Socket for RSB1A relay, with clip | 8 | pc |  |  | Panel design | Added
250 | B | Main PLC panel – Drop 0 (control room) | PLC-MAIN | NSYTRV42 | Linergy TR screw terminal block 4 mm², feed-through | 150 | pc |  |  | Panel design | Added | Estimate; confirm from wiring diagrams.
260 | B | Main PLC panel – Drop 0 (control room) | PLC-MAIN | TBC-ENC-PLC | Floor-standing enclosure 2000 × 800 × 600 IP55, fan, light, socket, earthing | 1 | pc |  |  | Panel design | Added – ref. TBC | Spacial SM or equivalent.
[5 empty] | Subtotal B – Main PLC panel – Drop 0 (control room) |  |  |  | 6241.7025 |  | 6 lines RFQ
| C | Rack 2 panel – Drop 1, MV / BESS / DG I/O and device network (11 kV GIS room)
270 | C | Rack 2 panel – Drop 1, MV / BESS / DG I/O and device network (11 kV GIS room) | PLC-R2 | BMEXBP1200 | PLC 12-slot Ethernet backplane | 1 | pc | 322.7805 | 322.7805 | Offer | Offered
280 | C | Rack 2 panel – Drop 1, MV / BESS / DG I/O and device network (11 kV GIS room) | PLC-R2 | BMXCPS3020 | X80 DC power supply 24–48 V DC, 32 W, isolated | 1 | pc | 320.0265 | 320.0265 | Offer | Offered
290 | C | Rack 2 panel – Drop 1, MV / BESS / DG I/O and device network (11 kV GIS room) | PLC-R2 | BMECRA31210 | X80 performance Ethernet drop adapter | 1 | pc | 789.4575 | 789.4575 | Offer | Offered
300 | C | Rack 2 panel – Drop 1, MV / BESS / DG I/O and device network (11 kV GIS room) | PLC-R2 | BMXDDI3202K | X80 digital input module 32 ch 24 V DC sink | 5 | pc | 212.1705 | 1060.8525 | I/O list | Offered | Offer 3; +2 for 138 hard-wired DI + 20 % spare (see IO Capacity).
310 | C | Rack 2 panel – Drop 1, MV / BESS / DG I/O and device network (11 kV GIS room) | PLC-R2 | BMXDDO3202K | X80 digital output module 32 ch 24 V DC source | 2 | pc | 250.218 | 500.436 | Offer | Offered
320 | C | Rack 2 panel – Drop 1, MV / BESS / DG I/O and device network (11 kV GIS room) | PLC-R2 | BMXFCW303 | 3 m pre-equipped cable, 1 connector + free wires (one per 32-ch module) | 7 | pc | 51.5835 | 361.0845 | I/O list | Offered | One per module (5 DI + 2 DO).
330 | C | Rack 2 panel – Drop 1, MV / BESS / DG I/O and device network (11 kV GIS room) | PLC-R2 | BMXNOM0200 | X80 serial link module, Modbus RTU, 2 × RS485 – DG controllers | 1 | pc | 414.8775 | 414.8775 | Offer | Offered
340 | C | Rack 2 panel – Drop 1, MV / BESS / DG I/O and device network (11 kV GIS room) | PLC-R2 | VW3A8306R10 | RS485 cordset 1 m, 2 × RJ45 | 1 | pc | 7.965 | 7.965 | Offer | Offered
350 | C | Rack 2 panel – Drop 1, MV / BESS / DG I/O and device network (11 kV GIS room) | SW2 | TBC-MCSESM-FO | Modicon managed switch 8TX + 2 FX single-mode – device network (SW2) | 1 | pc |  |  | Sheet 002 | Added – ref. TBC | Replaces offer MCSESM083F23F1 (copper only) so SW2 can close the fibre ring.
360 | C | Rack 2 panel – Drop 1, MV / BESS / DG I/O and device network (11 kV GIS room) | PLC-R2 | ABL8RPS24100 | Phaseo power supply 24 V DC 10 A | 2 | pc |  |  | Panel design | Added
370 | C | Rack 2 panel – Drop 1, MV / BESS / DG I/O and device network (11 kV GIS room) | PLC-R2 | ABL8RED24400 | Phaseo redundancy module 24 V DC 40 A | 1 | pc |  |  | Panel design | Added
380 | C | Rack 2 panel – Drop 1, MV / BESS / DG I/O and device network (11 kV GIS room) | PLC-R2 | RSB1A120BD | Zelio RSB interposing relay 1 C/O 12 A, 24 V DC coil – VCB / ACB / DG commands | 32 | pc |  |  | I/O list | Added | 26 DO in I/O list + spare.
390 | C | Rack 2 panel – Drop 1, MV / BESS / DG I/O and device network (11 kV GIS room) | PLC-R2 | RSZE1S35M | Socket for RSB1A relay, with clip | 32 | pc |  |  | Panel design | Added
400 | C | Rack 2 panel – Drop 1, MV / BESS / DG I/O and device network (11 kV GIS room) | PLC-R2 | NSYTRV42 | Linergy TR screw terminal block 4 mm², feed-through | 400 | pc |  |  | Panel design | Added | Estimate; 164 DI/DO + commons + supplies.
410 | C | Rack 2 panel – Drop 1, MV / BESS / DG I/O and device network (11 kV GIS room) | PLC-R2 | TBC-ENC-PLC | Floor-standing enclosure 2000 × 800 × 600 IP55, fan, light, socket, earthing | 1 | pc |  |  | Panel design | Added – ref. TBC
[5 empty] | Subtotal C – Rack 2 panel – Drop 1, MV / BESS / DG I/O and device network (11 kV GIS room) |  |  |  | 3777.48 |  | 7 lines RFQ
| D | 11 kV GIS combiner panel – protection relays
420 | D | 11 kV GIS combiner panel – protection relays | P5M30-AH1…AH8 | REL50458 | Easergy P5M30 48–250 V, 3 CT, 1 CSH, 4 VT, 16 DI / 12 DO, RSTP, Ethernet RJ45 | 8 | pc |  |  | Offer (PDF) | Offered | Price not in offer workbook. Confirm GIS panel vendor does not already supply relays.
[5 empty] | Subtotal D – 11 kV GIS combiner panel – protection relays |  |  |  | 0 |  | 1 lines RFQ
| E1 | President office TX station – LVDB 1 (NTS-LVP1/LVP2)
430 | E1 | President office TX station – LVDB 1 (NTS-LVP1/LVP2) | NTS-LVP1/2 | NTSNEC1200K | Edge I/O NTS network interface module + base + termination, EtherNet/IP | 2 | pc | 308.772 | 617.544 | Offer | Offered
440 | E1 | President office TX station – LVDB 1 (NTS-LVP1/LVP2) | NTS-LVP1/2 | NTSPFB1002HK | Edge I/O NTS power supply module + base, 24 V DC, bus and field | 2 | pc | 88.695 | 177.39 | Offer | Offered
450 | E1 | President office TX station – LVDB 1 (NTS-LVP1/LVP2) | NTS-LVP1/2 | NTSXTB02030H | Screw terminal block 2 pt, 5 mm, for power supply module | 4 | pc | 18 | 72 | Offer | Offered | 2 per power supply module.
460 | E1 | President office TX station – LVDB 1 (NTS-LVP1/LVP2) | NTS-LVP1/2 | NTSDDI1602XK | Edge I/O NTS discrete input 16 ch 24 V DC sink + base | 4 | pc | 122.2884 | 489.1536 | Offer | Offered | 29 DI required.
470 | E1 | President office TX station – LVDB 1 (NTS-LVP1/LVP2) | NTS-LVP1/2 | NTSXTB18001XH | Screw terminal block 18 pt, 5 mm, high-height (DI) | 4 | pc | 63 | 252 | Offer | Offered | One per DI module (offer had 3).
480 | E1 | President office TX station – LVDB 1 (NTS-LVP1/LVP2) | NTS-LVP1/2 | NTSDDO1602K | Edge I/O NTS discrete output 16 ch 24 V DC 0.5 A + base | 2 | pc | 137.268 | 274.536 | Offer | Offered | 11 DO required (incomer + 10 shunt trips).
490 | E1 | President office TX station – LVDB 1 (NTS-LVP1/LVP2) | NTS-LVP1/2 | NTSXTB18001H | Screw terminal block 18 pt, 3.81 mm, low-height (DO) | 2 | pc | 58 | 116 | Offer | Offered | One per DO module (offer had 1).
500 | E1 | President office TX station – LVDB 1 (NTS-LVP1/LVP2) | NTS-LVP1 | NTSFMB0120K | Edge I/O NTS field device master, RS485 / RS232 Modbus RTU | 1 | pc | 800 | 800 | Offer | Offered | Spare serial port for future meters.
510 | E1 | President office TX station – LVDB 1 (NTS-LVP1/LVP2) | NTS-LVP1 | NTSXTB12001H | Screw terminal block 12 pt, 5 mm (serial module) | 1 | pc | 40 | 40 | Offer | Offered
520 | E1 | President office TX station – LVDB 1 (NTS-LVP1/LVP2) | PAS600-LVP1/2 | PAS600 | EcoStruxure Universal Panel Server 110–277 V AC/DC | 2 | pc | 1106 | 2212 | Offer | Offered
530 | E1 | President office TX station – LVDB 1 (NTS-LVP1/LVP2) | PAS600-LVP1/2 | 130729 | Asset Link humidity sensor CL110 | 2 | pc | 99 | 198 | Offer | Offered
540 | E1 | President office TX station – LVDB 1 (NTS-LVP1/LVP2) | PAS600-LVP1/2 | EMS59440 | Asset Link temperature sensor TH110 | 4 | pc | 230 | 920 | Offer | Offered
550 | E1 | President office TX station – LVDB 1 (NTS-LVP1/LVP2) | PM5320-LVP | METSEPM5320 | PM5320 power meter, Ethernet, harmonics to 31st, 2 DI / 2 DO | 1 | pc |  |  | Offer (PDF) | Offered | Price not in offer workbook.
560 | E1 | President office TX station – LVDB 1 (NTS-LVP1/LVP2) | LS-LVP | TBC-MCSESM-FO | Modicon managed switch 8TX + 2 FX single-mode – field switch | 1 | pc |  |  | Sheet 002 | Added – ref. TBC
570 | E1 | President office TX station – LVDB 1 (NTS-LVP1/LVP2) | NTS-LVP | TBC-ENC-RIO | Wall-mounted enclosure 800 × 600 × 300 IP55 for Edge I/O, switch and PSU | 1 | pc |  |  | Panel design | Added – ref. TBC
580 | E1 | President office TX station – LVDB 1 (NTS-LVP1/LVP2) | NTS-LVP | ABL8RPS24050 | Phaseo power supply 24 V DC 5 A | 1 | pc |  |  | Panel design | Added | Feed from RMU UPS 2 kVA.
590 | E1 | President office TX station – LVDB 1 (NTS-LVP1/LVP2) | NTS-LVP | RSB1A120BD | Zelio RSB interposing relay 1 C/O 12 A, 24 V DC coil – shunt trips | 12 | pc |  |  | I/O list | Added
600 | E1 | President office TX station – LVDB 1 (NTS-LVP1/LVP2) | NTS-LVP | RSZE1S35M | Socket for RSB1A relay, with clip | 12 | pc |  |  | Panel design | Added
[5 empty] | Subtotal E1 – President office TX station – LVDB 1 (NTS-LVP1/LVP2) |  |  |  | 6168.6236 |  | 6 lines RFQ
| E2 | Prime Minister office TX station – LVDB 2 (NTS-LVM1)
610 | E2 | Prime Minister office TX station – LVDB 2 (NTS-LVM1) | NTS-LVM1 | NTSNEC1200K | Edge I/O NTS network interface module + base + termination, EtherNet/IP | 1 | pc | 308.772 | 308.772 | Offer | Offered
620 | E2 | Prime Minister office TX station – LVDB 2 (NTS-LVM1) | NTS-LVM1 | NTSPFB1002HK | Edge I/O NTS power supply module + base, 24 V DC, bus and field | 1 | pc | 88.695 | 88.695 | Offer | Offered
630 | E2 | Prime Minister office TX station – LVDB 2 (NTS-LVM1) | NTS-LVM1 | NTSXTB02030H | Screw terminal block 2 pt, 5 mm, for power supply module | 2 | pc | 18 | 36 | Offer | Offered
640 | E2 | Prime Minister office TX station – LVDB 2 (NTS-LVM1) | NTS-LVM1 | NTSDDI1602XK | Edge I/O NTS discrete input 16 ch 24 V DC sink + base | 3 | pc | 122.2884 | 366.8652 | Offer | Offered | 29 DI required.
650 | E2 | Prime Minister office TX station – LVDB 2 (NTS-LVM1) | NTS-LVM1 | NTSXTB18001XH | Screw terminal block 18 pt, 5 mm, high-height (DI) | 3 | pc | 63 | 189 | Offer | Offered
660 | E2 | Prime Minister office TX station – LVDB 2 (NTS-LVM1) | NTS-LVM1 | NTSDDO1602K | Edge I/O NTS discrete output 16 ch 24 V DC 0.5 A + base | 1 | pc | 137.268 | 137.268 | Offer | Offered | 11 DO required.
670 | E2 | Prime Minister office TX station – LVDB 2 (NTS-LVM1) | NTS-LVM1 | NTSXTB18001H | Screw terminal block 18 pt, 3.81 mm, low-height (DO) | 1 | pc | 58 | 58 | Offer | Offered
680 | E2 | Prime Minister office TX station – LVDB 2 (NTS-LVM1) | NTS-LVM1 | NTSFMB0120K | Edge I/O NTS field device master, RS485 / RS232 Modbus RTU | 1 | pc | 800 | 800 | Offer | Offered
690 | E2 | Prime Minister office TX station – LVDB 2 (NTS-LVM1) | NTS-LVM1 | NTSXTB12001H | Screw terminal block 12 pt, 5 mm (serial module) | 1 | pc | 40 | 40 | Offer | Offered
700 | E2 | Prime Minister office TX station – LVDB 2 (NTS-LVM1) | PAS600-LVM1 | PAS600 | EcoStruxure Universal Panel Server 110–277 V AC/DC | 1 | pc | 1106 | 1106 | Offer | Offered
710 | E2 | Prime Minister office TX station – LVDB 2 (NTS-LVM1) | PAS600-LVM1 | 130729 | Asset Link humidity sensor CL110 | 1 | pc | 99 | 99 | Offer | Offered
720 | E2 | Prime Minister office TX station – LVDB 2 (NTS-LVM1) | PAS600-LVM1 | EMS59440 | Asset Link temperature sensor TH110 | 1 | pc | 230 | 230 | Offer | Offered
730 | E2 | Prime Minister office TX station – LVDB 2 (NTS-LVM1) | PM5320-LVM | METSEPM5320 | PM5320 power meter, Ethernet, harmonics to 31st, 2 DI / 2 DO | 1 | pc |  |  | Offer (PDF) | Offered
740 | E2 | Prime Minister office TX station – LVDB 2 (NTS-LVM1) | LS-LVM | TBC-MCSESM-FO | Modicon managed switch 8TX + 2 FX single-mode – field switch | 1 | pc |  |  | Sheet 002 | Added – ref. TBC
750 | E2 | Prime Minister office TX station – LVDB 2 (NTS-LVM1) | NTS-LVM | TBC-ENC-RIO | Wall-mounted enclosure 800 × 600 × 300 IP55 for Edge I/O, switch and PSU | 1 | pc |  |  | Panel design | Added – ref. TBC
760 | E2 | Prime Minister office TX station – LVDB 2 (NTS-LVM1) | NTS-LVM | ABL8RPS24050 | Phaseo power supply 24 V DC 5 A | 1 | pc |  |  | Panel design | Added
770 | E2 | Prime Minister office TX station – LVDB 2 (NTS-LVM1) | NTS-LVM | RSB1A120BD | Zelio RSB interposing relay 1 C/O 12 A, 24 V DC coil – shunt trips | 12 | pc |  |  | I/O list | Added
780 | E2 | Prime Minister office TX station – LVDB 2 (NTS-LVM1) | NTS-LVM | RSZE1S35M | Socket for RSB1A relay, with clip | 12 | pc |  |  | Panel design | Added
[5 empty] | Subtotal E2 – Prime Minister office TX station – LVDB 2 (NTS-LVM1) |  |  |  | 3459.6002 |  | 6 lines RFQ
| F | PV inverter station – PV areas 1–4 (NTS-PV1…PV4)
790 | F | PV inverter station – PV areas 1–4 (NTS-PV1…PV4) | NTS-PV1…4 | NTSNEC1200K | Edge I/O NTS network interface module + base + termination, EtherNet/IP | 4 | pc | 308.772 | 1235.088 | Offer | Offered | One island per PV area.
800 | F | PV inverter station – PV areas 1–4 (NTS-PV1…PV4) | NTS-PV1…4 | NTSPFB1002HK | Edge I/O NTS power supply module + base, 24 V DC, bus and field | 4 | pc | 88.695 | 354.78 | Offer | Offered
810 | F | PV inverter station – PV areas 1–4 (NTS-PV1…PV4) | NTS-PV1…4 | NTSXTB02030H | Screw terminal block 2 pt, 5 mm, for power supply module | 8 | pc | 18 | 144 | Offer | Offered
820 | F | PV inverter station – PV areas 1–4 (NTS-PV1…PV4) | NTS-PV1…4 | NTSDDI1602XK | Edge I/O NTS discrete input 16 ch 24 V DC sink + base | 12 | pc | 122.2884 | 1467.4608 | Offer | Offered | Offer 3 per area; 4 DI needed per area – see Changes, option O1.
830 | F | PV inverter station – PV areas 1–4 (NTS-PV1…PV4) | NTS-PV1…4 | NTSXTB18001XH | Screw terminal block 18 pt, 5 mm, high-height (DI) | 12 | pc | 63 | 756 | Offer | Offered
840 | F | PV inverter station – PV areas 1–4 (NTS-PV1…PV4) | NTS-PV1…4 | NTSDDO1602K | Edge I/O NTS discrete output 16 ch 24 V DC 0.5 A + base | 4 | pc | 137.268 | 549.072 | Offer | Offered | No hard-wired DO needed in PV areas – see option O1.
850 | F | PV inverter station – PV areas 1–4 (NTS-PV1…PV4) | NTS-PV1…4 | NTSXTB18001H | Screw terminal block 18 pt, 3.81 mm, low-height (DO) | 4 | pc | 58 | 232 | Offer | Offered
860 | F | PV inverter station – PV areas 1–4 (NTS-PV1…PV4) | NTS-PV1…4 | NTSFMB0120K | Edge I/O NTS field device master, RS485 Modbus RTU – one SG350HX each | 4 | pc | 800 | 3200 | Offer | Offered | Point-to-point to each inverter (sheet 002, note 4).
870 | F | PV inverter station – PV areas 1–4 (NTS-PV1…PV4) | NTS-PV1…4 | NTSXTB12001H | Screw terminal block 12 pt, 5 mm (serial module) | 4 | pc | 40 | 160 | Offer | Offered
880 | F | PV inverter station – PV areas 1–4 (NTS-PV1…PV4) | PAS600-PV1…4 | PAS600 | EcoStruxure Universal Panel Server 110–277 V AC/DC | 4 | pc | 1106 | 4424 | Offer | Offered
890 | F | PV inverter station – PV areas 1–4 (NTS-PV1…PV4) | PAS600-PV1…4 | 130729 | Asset Link humidity sensor CL110 | 4 | pc | 99 | 396 | Offer | Offered
900 | F | PV inverter station – PV areas 1–4 (NTS-PV1…PV4) | PAS600-PV1…4 | EMS59440 | Asset Link temperature sensor TH110 | 4 | pc | 230 | 920 | Offer | Offered
910 | F | PV inverter station – PV areas 1–4 (NTS-PV1…PV4) | PM5320-PV | METSEPM5320 | PM5320 power meter, Ethernet, harmonics to 31st, 2 DI / 2 DO | 1 | pc |  |  | Offer (PDF) | Offered | 0.8 kV PV LV busbar; confirm CT/VT suitability at 800 V.
920 | F | PV inverter station – PV areas 1–4 (NTS-PV1…PV4) | LS-PV | TBC-MCSESM-FO | Modicon managed switch 8TX + 2 FX single-mode – field switch | 1 | pc |  |  | Sheet 002 | Added – ref. TBC
930 | F | PV inverter station – PV areas 1–4 (NTS-PV1…PV4) | NTS-PV | TBC-ENC-RIO | Wall-mounted enclosure 800 × 600 × 300 IP55 for Edge I/O, switch and PSU | 2 | pc |  |  | Panel design | Added – ref. TBC | Two enclosures for 4 islands; confirm against inverter layout.
940 | F | PV inverter station – PV areas 1–4 (NTS-PV1…PV4) | NTS-PV | ABL8RPS24050 | Phaseo power supply 24 V DC 5 A | 2 | pc |  |  | Panel design | Added
[5 empty] | Subtotal F – PV inverter station – PV areas 1–4 (NTS-PV1…PV4) |  |  |  | 13838.4008 |  | 4 lines RFQ
| G | BESS container interface
950 | G | BESS container interface | PM5320-BESS | METSEPM5320 | PM5320 power meter, Ethernet, harmonics to 31st, 2 DI / 2 DO | 1 | pc |  |  | Offer (PDF) | Offered | 0.69 kV BESS LV busbar.
960 | G | BESS container interface | LS-BESS | TBC-MCSESM-FO | Modicon managed switch 8TX + 2 FX single-mode – field switch | 1 | pc |  |  | Sheet 002 | Added – ref. TBC | Mount in vendor-provided space in container.
[5 empty] | Subtotal G – BESS container interface |  |  |  | 0 |  | 2 lines RFQ
| H | Diesel generator area
970 | H | Diesel generator area | PM5320-DG | METSEPM5320 | PM5320 power meter, Ethernet, harmonics to 31st, 2 DI / 2 DO | 1 | pc |  |  | Offer (PDF) | Offered | DG 0.4 kV common bus.
980 | H | Diesel generator area | LS-DG | TBC-MCSESM-FO | Modicon managed switch 8TX + 2 FX single-mode – field switch | 1 | pc |  |  | Sheet 002 | Added – ref. TBC
[5 empty] | Subtotal H – Diesel generator area |  |  |  | 0 |  | 2 lines RFQ
| J | Communication cabling and infrastructure
990 | J | Communication cabling and infrastructure | FO ring | TBC-FO-OS2-4C | Fibre optic cable single-mode OS2, 4 core, armoured, outdoor | 1500 | m |  |  | Sheet 002 | Added – ref. TBC | Estimate – take lengths from LV cable route drawings.
1000 | J | Communication cabling and infrastructure | FO ring | TBC-FO-PP | Fibre patch panel / splice box, 6 × LC duplex, with pigtails | 6 | pc |  |  | Sheet 002 | Added – ref. TBC | Control room + 5 field switches.
1010 | J | Communication cabling and infrastructure | FO ring | TBC-FO-PC | Fibre patch cord LC–LC duplex single-mode 2 m | 12 | pc |  |  | Sheet 002 | Added – ref. TBC
1020 | J | Communication cabling and infrastructure | Ethernet | TBC-CAT6 | Cat6 S/FTP industrial Ethernet cable | 500 | m |  |  | Sheet 002 | Added – ref. TBC | Estimate.
1030 | J | Communication cabling and infrastructure | Ethernet | TBC-RJ45 | RJ45 shielded field-installable connector, Cat6 | 100 | pc |  |  | Sheet 002 | Added – ref. TBC
1040 | J | Communication cabling and infrastructure | RS485 | TBC-RS485 | RS485 cable 2-pair shielded twisted pair 120 Ω (Belden 3106A or equal) | 600 | m |  |  | Sheet 002 | Added – ref. TBC | 4 inverters + DG controllers; estimate.
1050 | J | Communication cabling and infrastructure | Hard-wired I/O | TBC-MULTICORE | Screened multicore 1.0 mm² control cable for DI / DO | 1 | lot |  |  | Sheet 001 | Added – ref. TBC | Often by electrical contractor – confirm.
[5 empty] | Subtotal J – Communication cabling and infrastructure |  |  |  | 0 |  | 7 lines RFQ
| K | Third-party interfaces (by others – listed for completeness)
1060 | K | Third-party interfaces (by others – listed for completeness) | INV NB01…04 | SG350HX-RS485 | Sungrow SG350HX RS485 Modbus RTU port and register map | 4 | pc | 0 | 0 | Sheet 003 | By others | PV EPC scope.
1070 | K | Third-party interfaces (by others – listed for completeness) | BESS-EMS | BESS-EMS-MBTCP | BESS EMS Modbus TCP server, register map and heartbeat | 1 | lot | 0 | 0 | Sheet 004 | By others | BESS vendor scope.
1080 | K | Third-party interfaces (by others – listed for completeness) | DGC-1/2 | DGC-MBRTU | Genset controller Modbus RTU communication module | 2 | pc | 0 | 0 | Sheet 001 | By others | DG vendor scope; controller make TBC.
1090 | K | Third-party interfaces (by others – listed for completeness) | WS-01 | BLUELOG-XM5000 | Meteocontrol blue'Log XM 5000 weather station with sensors | 1 | lot | 0 | 0 | Sheet 003 | By others | PV EPC scope (drawing Weather Station Mast).
1100 | K | Third-party interfaces (by others – listed for completeness) | UPS-02/03 | RMU-UPS-CARD | Communication card for RMU 2 kVA UPS (Modbus TCP / SNMP) | 2 | pc | 0 | 0 | Sheet 002 | By others | RMU vendor scope; confirm availability.
1110 | K | Third-party interfaces (by others – listed for completeness) | FACP-GW | TBC-FACP-GW | Fire alarm panel Modbus gateway / volt-free output card | 1 | pc |  |  | Sheet 002 | Added – ref. TBC | Fire contractor to confirm; priced as SCADA item until agreed.
[5 empty] | Subtotal K – Third-party interfaces (by others – listed for completeness) |  |  |  | 0 |  | 1 lines RFQ
| L | Engineering and services
1120 | L | Engineering and services | — | SVC-DESIGN-COMM | System design and commissioning (lot, per offer) | 1 | lot | 37567 | 37567 | Offer | Offered | Confirm it includes FAT, SAT, training and as-built documents.
1130 | L | Engineering and services | — | TBC-SVC-FO | Fibre installation, splicing and OTDR testing | 1 | lot |  |  | Sheet 002 | Added – ref. TBC
[5 empty] | Subtotal L – Engineering and services |  |  |  | 37567 |  | 1 lines RFQ
| S | Commissioning and operational spares
1140 | S | Commissioning and operational spares | Spare | BMEXBP0800 | PLC 8-slot Ethernet backplane | 1 | pc | 227.682 | 227.682 | Offer | Offered
1150 | S | Commissioning and operational spares | Spare | BMXCPS3020 | X80 DC power supply 24–48 V DC | 1 | pc | 320.0265 | 320.0265 | Offer | Offered
1160 | S | Commissioning and operational spares | Spare | BMEP582040 | M580 CPU level 2 | 1 | pc | 2337.7635 | 2337.7635 | Offer | Offered | Cold spare. Not a hot-standby pair.
1170 | S | Commissioning and operational spares | Spare | BMENOC0311 | M580 I/O scanner module, 3 ports | 1 | pc | 887.94 | 887.94 | Offer | Offered
1180 | S | Commissioning and operational spares | Spare | BMXDDI3202K | X80 digital input module 32 ch | 1 | pc | 212.1705 | 212.1705 | Offer | Offered
1190 | S | Commissioning and operational spares | Spare | BMXDDO3202K | X80 digital output module 32 ch | 1 | pc | 250.218 | 250.218 | Offer | Offered
1200 | S | Commissioning and operational spares | Spare | NTSNEC1200K | Edge I/O NTS network interface module | 1 | pc | 308.772 | 308.772 | Offer | Offered
1210 | S | Commissioning and operational spares | Spare | NTSPFB1002HK | Edge I/O NTS power supply module | 1 | pc | 88.695 | 88.695 | Offer | Offered
1220 | S | Commissioning and operational spares | Spare | NTSDDI1602XK | Edge I/O NTS discrete input 16 ch | 1 | pc | 122.2884 | 122.2884 | Offer | Offered
1230 | S | Commissioning and operational spares | Spare | NTSDDO1602K | Edge I/O NTS discrete output 16 ch | 1 | pc | 137.268 | 137.268 | Offer | Offered
1240 | S | Commissioning and operational spares | Spare | PAS600 | EcoStruxure Universal Panel Server | 1 | pc | 1106 | 1106 | Offer | Offered
1250 | S | Commissioning and operational spares | Spare | 130729 | Asset Link humidity sensor CL110 | 1 | pc | 99 | 99 | Offer | Offered
1260 | S | Commissioning and operational spares | Spare | EMS59440 | Asset Link temperature sensor TH110 | 1 | pc | 230 | 230 | Offer | Offered
1270 | S | Commissioning and operational spares | Spare | TBC-MCSESM-FO | Managed switch 8TX + 2 FX single-mode | 1 | pc |  |  | Sheet 002 | Added – ref. TBC | Covers SW2 and 5 field switches.
1280 | S | Commissioning and operational spares | Spare | RSB1A120BD | Zelio RSB interposing relay | 5 | pc |  |  | Panel design | Added
[5 empty] | Subtotal S – Commissioning and operational spares |  |  |  | 6327.8239 |  | 2 lines RFQ
[5 empty] | TOTAL – priced lines only |  |  |  | 104639.1865
[5 empty] | Lines awaiting price (RFQ) |  |  |  | 53
[5 empty] | Offer total for comparison (Schneider workbook, incl. services) |  |  |  | 102584.4101
Note on J174: Source: offer workbook 'Bill of Material for Villa Somalia', sheet 'BOM by Reference', Total value. Excludes P5M30 and PM5320 (no price given).

## BOM by Reference
Bill of Material by Reference (quantities summed from 'BOM by Location')
Reference | Description | Total qty | Unit | Unit price | Total price | Status | Offer qty | Change
HMIP67GD0F88BE7N00 | Harmony P6 industrial PC – operator stations (configuration per offer) | 2 | pc | 6750 | 13500 | Offered | 2 | 0
HMIEMSE3PRT4KA | EcoStruxure Machine SCADA Expert 3rd-party runtime 4K tags, digital licence | 2 | pc | 4699.914 | 9399.8279 | Offered | 2 | 0
HMIEMSEBT4KA | EcoStruxure Machine SCADA Expert build-time 4K tags, digital licence | 1 | pc | 2749.0325 | 2749.0325 | Offered | 1 | 0
TBC-SRV-01 | SCADA server / historian, rack industrial server, RAID 1, redundant PSU, 13-month storage | 1 | pc |  |  | Added – ref. TBC | 0 | 1
TBC-ENG-01 | Engineering workstation (laptop) with EcoStruxure Control Expert licence for M580 | 1 | pc |  |  | Added – ref. TBC | 0 | 1
TBC-GPS-01 | GPS master clock with antenna, NTP / PTP server | 1 | pc |  |  | Added – ref. TBC | 0 | 1
TBC-FW-01 | Industrial firewall, DMZ between Level 2 and Level 3 | 1 | pc |  |  | Added – ref. TBC | 0 | 1
MCSESM083F23F1 | Modicon Extended Managed Switch 8TX – SCADA LAN (SW1) | 1 | pc | 1609.695 | 1609.695 | Offered | 2 | -1
SRT6KRMXLI | APC Smart-UPS SRT 6 kVA rack/tower, 230 V – SCADA, PLC and switches | 1 | pc |  |  | Added | 0 | 1
AP9641 | UPS Network Management Card 3 (SNMP / Modbus TCP) | 1 | pc |  |  | Added | 0 | 1
AR3100 | NetShelter SX 42U 600 × 1070 mm rack – server, SW1, FW-01, GPS-01, UPS-01 | 1 | pc |  |  | Added | 0 | 1
TBC-CONSOLE | Operator console, 2 positions, 2 × 27" monitors each, keyboard / mouse | 1 | lot |  |  | Added – ref. TBC | 0 | 1
BMEXBP0800 | PLC 8-slot Ethernet backplane | 2 | pc | 227.682 | 455.364 | Offered | 2 | 0
BMXCPS3020 | X80 DC power supply 24–48 V DC, 32 W, isolated | 3 | pc | 320.0265 | 960.0795 | Offered | 3 | 0
BMEP582040 | M580 CPU level 2, remote and distributed I/O – plant controller (PPC) | 2 | pc | 2337.7635 | 4675.527 | Offered | 2 | 0
BMENOC0311 | M580 I/O scanner module, FactoryCast, EtherNet/IP & Modbus TCP, 3 ports | 3 | pc | 887.94 | 2663.82 | Offered | 2 | 1
BMENOC0321 | M580 I/O scanner module, IP forwarding, coated – device network | 1 | pc | 1014.795 | 1014.795 | Offered | 1 | 0
BMXDDI3202K | X80 digital input module 32 ch 24 V DC sink | 7 | pc | 212.1705 | 1485.1935 | Offered | 5 | 2
BMXDDO3202K | X80 digital output module 32 ch 24 V DC source | 4 | pc | 250.218 | 1000.872 | Offered | 4 | 0
BMXFCW303 | 3 m pre-equipped cable, 1 connector + free wires (one per 32-ch module) | 9 | pc | 51.5835 | 464.2515 | Offered | 7 | 2
ABL8RPS24100 | Phaseo power supply 24 V DC 10 A | 4 | pc |  |  | Added | 0 | 4
ABL8RED24400 | Phaseo redundancy module 24 V DC 40 A | 2 | pc |  |  | Added | 0 | 2
RSB1A120BD | Zelio RSB interposing relay 1 C/O 12 A, 24 V DC coil | 69 | pc |  |  | Added | 0 | 69
RSZE1S35M | Socket for RSB1A relay, with clip | 64 | pc |  |  | Added | 0 | 64
NSYTRV42 | Linergy TR screw terminal block 4 mm², feed-through | 550 | pc |  |  | Added | 0 | 550
TBC-ENC-PLC | Floor-standing enclosure 2000 × 800 × 600 IP55, fan, light, socket, earthing | 2 | pc |  |  | Added – ref. TBC | 0 | 2
BMEXBP1200 | PLC 12-slot Ethernet backplane | 1 | pc | 322.7805 | 322.7805 | Offered | 1 | 0
BMECRA31210 | X80 performance Ethernet drop adapter | 1 | pc | 789.4575 | 789.4575 | Offered | 1 | 0
BMXNOM0200 | X80 serial link module, Modbus RTU, 2 × RS485 – DG controllers | 1 | pc | 414.8775 | 414.8775 | Offered | 1 | 0
VW3A8306R10 | RS485 cordset 1 m, 2 × RJ45 | 1 | pc | 7.965 | 7.965 | Offered | 1 | 0
TBC-MCSESM-FO | Modicon managed switch 8TX + 2 FX single-mode – device network (SW2) | 7 | pc |  |  | Added – ref. TBC | 0 | 7
REL50458 | Easergy P5M30 48–250 V, 3 CT, 1 CSH, 4 VT, 16 DI / 12 DO, RSTP, Ethernet RJ45 | 8 | pc |  |  | Offered | 8 | 0
NTSNEC1200K | Edge I/O NTS network interface module + base + termination, EtherNet/IP | 8 | pc | 308.772 | 2470.176 | Offered | 7 | 1
NTSPFB1002HK | Edge I/O NTS power supply module + base, 24 V DC, bus and field | 8 | pc | 88.695 | 709.56 | Offered | 7 | 1
NTSXTB02030H | Screw terminal block 2 pt, 5 mm, for power supply module | 14 | pc | 18 | 252 | Offered | 12 | 2
NTSDDI1602XK | Edge I/O NTS discrete input 16 ch 24 V DC sink + base | 20 | pc | 122.2884 | 2445.768 | Offered | 19 | 1
NTSXTB18001XH | Screw terminal block 18 pt, 5 mm, high-height (DI) | 19 | pc | 63 | 1197 | Offered | 18 | 1
NTSDDO1602K | Edge I/O NTS discrete output 16 ch 24 V DC 0.5 A + base | 8 | pc | 137.268 | 1098.144 | Offered | 7 | 1
NTSXTB18001H | Screw terminal block 18 pt, 3.81 mm, low-height (DO) | 7 | pc | 58 | 406 | Offered | 6 | 1
NTSFMB0120K | Edge I/O NTS field device master, RS485 / RS232 Modbus RTU | 6 | pc | 800 | 4800 | Offered | 6 | 0
NTSXTB12001H | Screw terminal block 12 pt, 5 mm (serial module) | 6 | pc | 40 | 240 | Offered | 6 | 0
PAS600 | EcoStruxure Universal Panel Server 110–277 V AC/DC | 8 | pc | 1106 | 8848 | Offered | 7 | 1
130729 | Asset Link humidity sensor CL110 | 8 | pc | 99 | 792 | Offered | 7 | 1
EMS59440 | Asset Link temperature sensor TH110 | 10 | pc | 230 | 2300 | Offered | 9 | 1
METSEPM5320 | PM5320 power meter, Ethernet, harmonics to 31st, 2 DI / 2 DO | 5 | pc |  |  | Offered | 5 | 0
TBC-ENC-RIO | Wall-mounted enclosure 800 × 600 × 300 IP55 for Edge I/O, switch and PSU | 4 | pc |  |  | Added – ref. TBC | 0 | 4
ABL8RPS24050 | Phaseo power supply 24 V DC 5 A | 4 | pc |  |  | Added | 0 | 4
TBC-FO-OS2-4C | Fibre optic cable single-mode OS2, 4 core, armoured, outdoor | 1500 | m |  |  | Added – ref. TBC | 0 | 1500
TBC-FO-PP | Fibre patch panel / splice box, 6 × LC duplex, with pigtails | 6 | pc |  |  | Added – ref. TBC | 0 | 6
TBC-FO-PC | Fibre patch cord LC–LC duplex single-mode 2 m | 12 | pc |  |  | Added – ref. TBC | 0 | 12
TBC-CAT6 | Cat6 S/FTP industrial Ethernet cable | 500 | m |  |  | Added – ref. TBC | 0 | 500
TBC-RJ45 | RJ45 shielded field-installable connector, Cat6 | 100 | pc |  |  | Added – ref. TBC | 0 | 100
TBC-RS485 | RS485 cable 2-pair shielded twisted pair 120 Ω (Belden 3106A or equal) | 600 | m |  |  | Added – ref. TBC | 0 | 600
TBC-MULTICORE | Screened multicore 1.0 mm² control cable for DI / DO | 1 | lot |  |  | Added – ref. TBC | 0 | 1
SG350HX-RS485 | Sungrow SG350HX RS485 Modbus RTU port and register map | 4 | pc | 0 | 0 | By others | 0 | 4
BESS-EMS-MBTCP | BESS EMS Modbus TCP server, register map and heartbeat | 1 | lot | 0 | 0 | By others | 0 | 1
DGC-MBRTU | Genset controller Modbus RTU communication module | 2 | pc | 0 | 0 | By others | 0 | 2
BLUELOG-XM5000 | Meteocontrol blue'Log XM 5000 weather station with sensors | 1 | lot | 0 | 0 | By others | 0 | 1
RMU-UPS-CARD | Communication card for RMU 2 kVA UPS (Modbus TCP / SNMP) | 2 | pc | 0 | 0 | By others | 0 | 2
TBC-FACP-GW | Fire alarm panel Modbus gateway / volt-free output card | 1 | pc |  |  | Added – ref. TBC | 0 | 1
SVC-DESIGN-COMM | System design and commissioning (lot, per offer) | 1 | lot | 37567 | 37567 | Offered | 1 | 0
TBC-SVC-FO | Fibre installation, splicing and OTDR testing | 1 | lot |  |  | Added – ref. TBC | 0 | 1
| TOTAL – priced lines |  |  |  | 104639.1865
| Check: equals 'BOM by Location' total |  |  |  | OK

## Summary
Cost summary by location
Loc | Location | Priced subtotal | Lines RFQ | Share of priced total
A | Control room – SCADA, servers and network (Level 2/3) | 27258.5555 | 8 | 26.05%
B | Main PLC panel – Drop 0 (control room) | 6241.7025 | 6 | 5.965%
C | Rack 2 panel – Drop 1, MV / BESS / DG I/O and device network (11 kV GIS room) | 3777.48 | 7 | 3.61%
D | 11 kV GIS combiner panel – protection relays | 0 | 1 | 0%
E1 | President office TX station – LVDB 1 (NTS-LVP1/LVP2) | 6168.6236 | 6 | 5.895%
E2 | Prime Minister office TX station – LVDB 2 (NTS-LVM1) | 3459.6002 | 6 | 3.306%
F | PV inverter station – PV areas 1–4 (NTS-PV1…PV4) | 13838.4008 | 4 | 13.22%
G | BESS container interface | 0 | 2 | 0%
H | Diesel generator area | 0 | 2 | 0%
J | Communication cabling and infrastructure | 0 | 7 | 0%
K | Third-party interfaces (by others – listed for completeness) | 0 | 1 | 0%
L | Engineering and services | 37567 | 1 | 35.9%
S | Commissioning and operational spares | 6327.8239 | 2 | 6.047%
| Total | 104639.1865 | 53

## Changes vs Offer
Changes against the Schneider Electric offer (Villa Somalia, version 1)
Reference | Description | Offer qty | Project qty | Delta | Change | Reason
BMENOC0311 | M580 I/O scanner module, FactoryCast, EtherNet/IP & Modbus TCP, 3 ports | 2 | 3 | 1 | Quantity | Second NOC0311 for the second SCADA LAN path (sheet 001).
BMXDDI3202K | X80 digital input module 32 ch 24 V DC sink | 5 | 7 | 2 | Quantity | 138 hard-wired DI on the X80 racks + 20 % spare needs 6 modules; offer had 4 in use.
BMXFCW303 | 3 m pre-equipped cable, 1 connector + free wires (one per 32-ch module) | 7 | 9 | 2 | Quantity | One cable per 32-channel module (9 modules).
MCSESM083F23F1 | Modicon Extended Managed Switch 8TX – SCADA LAN (SW1) | 2 | 1 | -1 | Replaced | SW2 must close the fibre ring; copper-only switch replaced by an FX variant.
NTSNEC1200K | Edge I/O NTS network interface module + base + termination, EtherNet/IP | 7 | 8 | 1 | Quantity | 7 islands as drawn (President station has 2) + 1 spare.
NTSPFB1002HK | Edge I/O NTS power supply module + base, 24 V DC, bus and field | 7 | 8 | 1 | Quantity | One per island (7) + 1 spare.
NTSXTB02030H | Screw terminal block 2 pt, 5 mm, for power supply module | 12 | 14 | 2 | Quantity | Two terminal blocks per power supply module (7 modules).
NTSDDI1602XK | Edge I/O NTS discrete input 16 ch 24 V DC sink + base | 19 | 20 | 1 | Quantity | Location quantities add to 19 installed; spare was not on top.
NTSXTB18001XH | Screw terminal block 18 pt, 5 mm, high-height (DI) | 18 | 19 | 1 | Quantity | One terminal block per DI module (offer short by 1 at LVDB 1).
NTSDDO1602K | Edge I/O NTS discrete output 16 ch 24 V DC 0.5 A + base | 7 | 8 | 1 | Quantity | 7 installed + 1 spare.
NTSXTB18001H | Screw terminal block 18 pt, 3.81 mm, low-height (DO) | 6 | 7 | 1 | Quantity | One terminal block per DO module (offer short by 1 at LVDB 1).
PAS600 | EcoStruxure Universal Panel Server 110–277 V AC/DC | 7 | 8 | 1 | Quantity | 7 installed + 1 spare (offer spare not on top).
130729 | Asset Link humidity sensor CL110 | 7 | 8 | 1 | Quantity | 7 installed + 1 spare.
EMS59440 | Asset Link temperature sensor TH110 | 9 | 10 | 1 | Quantity | 9 installed + 1 spare.
PVSCL60E | Three-phase string inverter (Schneider) | 4 | 0 | -4 | Removed | Plant uses 4 × Sungrow SG350HX supplied by the PV EPC; Schneider string inverter not required.
TBC-SRV-01 | SCADA server / historian, rack industrial server, RAID 1, redundant PSU, 13-month storage | 0 | 1 | 1 | Added | Required by drawings 001/002 or panel design; not in offer.
TBC-ENG-01 | Engineering workstation (laptop) with EcoStruxure Control Expert licence for M580 | 0 | 1 | 1 | Added | Required by drawings 001/002 or panel design; not in offer.
TBC-GPS-01 | GPS master clock with antenna, NTP / PTP server | 0 | 1 | 1 | Added | Required by drawings 001/002 or panel design; not in offer.
TBC-FW-01 | Industrial firewall, DMZ between Level 2 and Level 3 | 0 | 1 | 1 | Added | Required by drawings 001/002 or panel design; not in offer.
SRT6KRMXLI | APC Smart-UPS SRT 6 kVA rack/tower, 230 V – SCADA, PLC and switches | 0 | 1 | 1 | Added | Required by drawings 001/002 or panel design; not in offer.
AP9641 | UPS Network Management Card 3 (SNMP / Modbus TCP) | 0 | 1 | 1 | Added | Required by drawings 001/002 or panel design; not in offer.
AR3100 | NetShelter SX 42U 600 × 1070 mm rack – server, SW1, FW-01, GPS-01, UPS-01 | 0 | 1 | 1 | Added | Required by drawings 001/002 or panel design; not in offer.
TBC-CONSOLE | Operator console, 2 positions, 2 × 27" monitors each, keyboard / mouse | 0 | 1 | 1 | Added | Required by drawings 001/002 or panel design; not in offer.
ABL8RPS24100 | Phaseo power supply 24 V DC 10 A | 0 | 4 | 4 | Added | Required by drawings 001/002 or panel design; not in offer.
ABL8RED24400 | Phaseo redundancy module 24 V DC 40 A | 0 | 2 | 2 | Added | Required by drawings 001/002 or panel design; not in offer.
RSB1A120BD | Zelio RSB interposing relay 1 C/O 12 A, 24 V DC coil | 0 | 69 | 69 | Added | Required by drawings 001/002 or panel design; not in offer.
RSZE1S35M | Socket for RSB1A relay, with clip | 0 | 64 | 64 | Added | Required by drawings 001/002 or panel design; not in offer.
NSYTRV42 | Linergy TR screw terminal block 4 mm², feed-through | 0 | 550 | 550 | Added | Required by drawings 001/002 or panel design; not in offer.
TBC-ENC-PLC | Floor-standing enclosure 2000 × 800 × 600 IP55, fan, light, socket, earthing | 0 | 2 | 2 | Added | Required by drawings 001/002 or panel design; not in offer.
TBC-MCSESM-FO | Modicon managed switch 8TX + 2 FX single-mode – device network (SW2) | 0 | 7 | 7 | Added | Required by drawings 001/002 or panel design; not in offer.
TBC-ENC-RIO | Wall-mounted enclosure 800 × 600 × 300 IP55 for Edge I/O, switch and PSU | 0 | 4 | 4 | Added | Required by drawings 001/002 or panel design; not in offer.
ABL8RPS24050 | Phaseo power supply 24 V DC 5 A | 0 | 4 | 4 | Added | Required by drawings 001/002 or panel design; not in offer.
TBC-FO-OS2-4C | Fibre optic cable single-mode OS2, 4 core, armoured, outdoor | 0 | 1500 | 1500 | Added | Required by drawings 001/002 or panel design; not in offer.
TBC-FO-PP | Fibre patch panel / splice box, 6 × LC duplex, with pigtails | 0 | 6 | 6 | Added | Required by drawings 001/002 or panel design; not in offer.
TBC-FO-PC | Fibre patch cord LC–LC duplex single-mode 2 m | 0 | 12 | 12 | Added | Required by drawings 001/002 or panel design; not in offer.
TBC-CAT6 | Cat6 S/FTP industrial Ethernet cable | 0 | 500 | 500 | Added | Required by drawings 001/002 or panel design; not in offer.
TBC-RJ45 | RJ45 shielded field-installable connector, Cat6 | 0 | 100 | 100 | Added | Required by drawings 001/002 or panel design; not in offer.
TBC-RS485 | RS485 cable 2-pair shielded twisted pair 120 Ω (Belden 3106A or equal) | 0 | 600 | 600 | Added | Required by drawings 001/002 or panel design; not in offer.
TBC-MULTICORE | Screened multicore 1.0 mm² control cable for DI / DO | 0 | 1 | 1 | Added | Required by drawings 001/002 or panel design; not in offer.
SG350HX-RS485 | Sungrow SG350HX RS485 Modbus RTU port and register map | 0 | 4 | 4 | Added | Required by drawings 001/002 or panel design; not in offer.
BESS-EMS-MBTCP | BESS EMS Modbus TCP server, register map and heartbeat | 0 | 1 | 1 | Added | Required by drawings 001/002 or panel design; not in offer.
DGC-MBRTU | Genset controller Modbus RTU communication module | 0 | 2 | 2 | Added | Required by drawings 001/002 or panel design; not in offer.
BLUELOG-XM5000 | Meteocontrol blue'Log XM 5000 weather station with sensors | 0 | 1 | 1 | Added | Required by drawings 001/002 or panel design; not in offer.
RMU-UPS-CARD | Communication card for RMU 2 kVA UPS (Modbus TCP / SNMP) | 0 | 2 | 2 | Added | Required by drawings 001/002 or panel design; not in offer.
TBC-FACP-GW | Fire alarm panel Modbus gateway / volt-free output card | 0 | 1 | 1 | Added | Required by drawings 001/002 or panel design; not in offer.
TBC-SVC-FO | Fibre installation, splicing and OTDR testing | 0 | 1 | 1 | Added | Required by drawings 001/002 or panel design; not in offer.
Options not applied (decision needed)
O1 | PV areas: 4 hard-wired DI per area need 1 × NTSDDI1602XK and no DO module. Reducing from 3 DI + 1 DO per area to 1 DI saves 8 × NTSDDI1602XK, 8 × NTSXTB18001XH, 4 × NTSDDO1602K and 4 × NTSXTB18001H. Not applied because drawing 003 and the offer show 3 DI + 1 DO; keep if combiner-box signals are expected.
O2 | Hot-standby controller: replace BMEP582040 + spare by an M580 hot-standby pair (BMEH58xxxx + sync link) if the client requires controller redundancy.
O3 | Relays P5M30 and PM5320 meters: remove from this BOM if the GIS panel / LV board vendors already supply them.

## IO Capacity
Hard-wired I/O capacity check
Spare required | 20% | Input. Required DI/DO counts come from docs/villa-somalia-io-list.csv (types DI and DO).
Area | Locations | Type | Required (I/O list) | Required incl. spare | Module | Channels / module | Modules installed | Channels installed | Free channels | Free % | Check
X80 racks (main + Rack 2) | B, C | DI | 138 | 166 | BMXDDI3202K | 32 | 6 | 192 | 54 | 28.12% | OK
X80 racks (main + Rack 2) | B, C | DO | 26 | 32 | BMXDDO3202K | 32 | 3 | 96 | 70 | 72.92% | OK
President TX station | E1 | DI | 29 | 35 | NTSDDI1602XK | 16 | 4 | 64 | 35 | 54.69% | OK
President TX station | E1 | DO | 11 | 14 | NTSDDO1602K | 16 | 2 | 32 | 21 | 65.62% | OK
Prime Minister TX station | E2 | DI | 29 | 35 | NTSDDI1602XK | 16 | 3 | 48 | 19 | 39.58% | OK
Prime Minister TX station | E2 | DO | 11 | 14 | NTSDDO1602K | 16 | 1 | 16 | 5 | 31.25% | OK
PV areas 1–4 (total) | F | DI | 16 | 20 | NTSDDI1602XK | 16 | 12 | 192 | 176 | 91.67% | OK
PV areas 1–4 (total) | F | DO | 0 | 0 | NTSDDO1602K | 16 | 4 | 64 | 64 | 100% | OK